## Register Map Legend
Summary
Block
Name of the data set.
Data Set
BDS - Basic Data Set
FDS - Full Data Set
Description
A short description of the register contents.
Units
Lists the units (Watts, Volts, Amps, etc.) of the value that the register holds.
Range
Defines the limits of the register value.
R/W
R = Read only. Used with both int or float formats
R/W = Read and Write. Writes are only done in integer format.
W = Write only. Writes are only done in integer format.
NV
Value is stored in non-volatile memory. The value shall still be available if the meter experiences a power loss and reset.
Modbus
Address
Modbus register addresses are in traditional Base 1 format. Modbus is Base 0 on the wire. Subtract one from the address in the table to get the address used on the wire.
# Registers
Number of registers in a data format or block.
Data Formats
| ASCII: |  | ASCII format character string. Null terminated. Each ASCII character is stored in a byte, with two characters per register. The first character is in the most significant byte of the first (lowest address) register, the second character is in the least significant byte of the first register, the third character is in the most significant byte of the second register, etc... When read using a block read command, the character stream is in order on the Modbus RTU wire. Fill from the lowest regiser first. Unused characters (bytes) should be filled with 0x00 (NULL).
| UInt: |  | Unsigned 16-bit integer. 1 Register. Range is 0 to 32767. 0x8000 indicates unavailable.
| SInt: |  | Signed 16-bit integer. 1 Register. Range is -32767 to +32767. 0x8000 indicates unavailable.
| ULong: |  | Unsigned 32-bit integer; Upper 16-bits (MSR) in lowest-numbered / first listed register (001/002 = MSR/LSR). 2 Registers. Used for accumulators. Returns 0x00000000 (no accumulation) if unavailable.
| SLong: |  | Signed 32-bit integer (31 bits effective); Upper 16-bits (MSR) in lowest-numbered / first listed register (001/002 = MSR/LSR). 2 Registers. Not used on this meter. Returns 0x80000000 if unavailable.
| Float: |  | 32-bit floating point; Upper 16-bits (MSR) in lowest-numbered / first listed register (257/258 = MSR/LSR). Encoding is per IEEE standard 754 single precision. 2 Registers. Returns 0x7FC00000 (Quite Not A Number) if unavailable.
Register Order
For 32 bit and larger words, shows the placement of the Most Significant Register (MSR) and Least Significant Register (LSR). Each register is a 16 bit word. The MSR is typically in the lower register address, the LSR in the upper. This lets a 32 bit or larger value be read using the Modbus block read command, and all 32 bits will be buffered in the correct order.
Integer Scale
Some Integer values must be multiplied by a scale factor (typically a fraction) to be read correctly. This is done to allow integer numbers to represent fractional numbers. The scale factor values are calculated by the meter when it is configured based on the Number of CTs, CT and PT ratios, etc. The scale factors only change if the meter configuration changes. There are scale factors for the integer Amps (I), Volts (V), Watts (W), and Energy (E) in the meter configuration area. The scale factor is a signed integer that translates to a multiplier to scale the integer to its units according to the following table:
|  | Scale Factor | Multiplier
|  | -6 | 1e-06
|  | -5 | 1e-05
|  | -4 | 0.0001
|  | -3 | 0.001
|  | -2 | 0.01
|  | -1 | 0.1
|  | 0 | 1
|  | 1 | 10
|  | 2 | 100
|  | 3 | 1000
|  | 4 | 10000
|  | 5 | 100000
|  | 6 | 1000000
Another way to look at the scale factor is that it tells the user where to put the decimal point. Examples with integer 123456: if the scale factor for this integer is -3, move the decimal point 3 positions to the left, resulting in the number 123.456. If the integer is +3, the decimal is moved 3 positions to the right and the number is interpreted as 123456000.0.

## Enercept Integer Conversion
H803x Integer Divisor Table |  | Enercept Divisor Table |  |  |  | Conversion factors apply to the Enercept emulation register block starting from address 1. Do not apply to other register blocks.
Register |  | From | 0 | 2 | 6 | 11 | 26 | 51 | 101 | 201 | 401 | 801 | 1601 | 3201 | 6401
|  | CT Amps | [7 empty] | 300 |  |  | 2400
Address | Units | To | 1 | 5 | 10 | 25 | 50 | 100 | 200 | 400 | 800 | 1600 | 3200 | 6400 | 12800
Units
1 | Real Energy Consumption, LSR | kWh | 12800 | 2560 | 1280 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2 | 1
2 | Real Energy Consumption, MSR | kWh | 0.19531 | 0.039062 | 0.019531 | 0.0078125 | 0.0039062 | 0.0019531 | 0.00097656 | 0.00048828 | 0.00024414 | 0.00012207 | 6.1035e-05 | 3.0518e-05 | 1.5259e-05
3 | Total Instantaneous Real Power (3 Phase Total) | kW | 25000 | 5000 | 2500 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125 | 3.9062 | 1.9531
4 | Total Instantaneous Reactive Power (3 Phase Total) | kVAR | 25000 | 5000 | 2500 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125 | 3.9062 | 1.9531
5 | Total Instantaneous Apparent Power (3 Phase Total) | kVA | 25000 | 5000 | 2500 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125 | 3.9062 | 1.9531
6 | Total Power Factor (Total KW / Total KVA) | PF | 32768 | same >>>
7 | Voltage, Line to Line, Average of Phases | Volts | 32 | same >>>
8 | Voltage, Line to Neutral, Average of Phases | Volts | 64 | same >>>
9 | Current, Average of Phases | Amps | 25600 | 5120 | 2560 | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2
10 | Real Power, Phase A | kW | 100000 | 20000 | 10000 | 4000 | 2000 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125
11 | Real Power, Phase B | kW | 100000 | 20000 | 10000 | 4000 | 2000 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125
12 | Real Power, Phase C | kW | 100000 | 20000 | 10000 | 4000 | 2000 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125
13 | Power Factor, Phase A | PF | 32768 | same >>>
14 | Power Factor, Phase B | PF | 32768 | same >>>
15 | Power Factor, Phase C | PF | 32768 | same >>>
16 | Voltage, Phase A-B | Volts | 32 | same >>>
17 | Voltage, Phase B-C | Volts | 32 | same >>>
18 | Voltage, Phase A-C | Volts | 32 | same >>>
19 | Voltage, Phase A-N | Volts | 64 | same >>>
20 | Voltage, Phase B-N | Volts | 64 | same >>>
21 | Voltage, Phase C-N | Volts | 64 | same >>>
22 | Current, Instantaneous, Phase A | Amps | 25600 | 5120 | 2560 | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2
23 | Current, Instantaneous, Phase B | Amps | 25600 | 5120 | 2560 | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2
24 | Current, Instantaneous, Phase C | Amps | 25600 | 5120 | 2560 | 1024 | 512 | 256 | 128 | 64 | 32 | 16 | 8 | 4 | 2
25 | Average Real Power (Reset by writing a 0) | kW | 25000 | 5000 | 2500 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125 | 3.9062 | 1.9531
26 | Minimum Real Power (Reset by writing a 0) | kW | 25000 | 5000 | 2500 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125 | 3.9062 | 1.9531
27 | Maximum Real Power (Reset by writing a 0) | kW | 25000 | 5000 | 2500 | 1000 | 500 | 250 | 125 | 62.5 | 31.25 | 15.625 | 7.8125 | 3.9062 | 1.9531
Note: Underlined CT Amps are the traditional Enercept CT sizes.

## EM4200 Register Map
Block | BDS | FDS | DESCRIPTION |  |  | UNITS | RANGE | R/W | NV | Modbus | Address | # Registers | Format | Register Order | Integer Scale
Enercept Meter Data (Basic and Enhanced) |  |  |  | Insensitive to CT orientation | [6 empty] | 1 | 109
Enercept Integer Data | [10 empty] | 1 | 39
Space allocated for future use. Not to be published in Schneider documentation. |  |  | Real Energy Consumption | Clear to 0 by writing a 0 to either register. |  | kWh | 0-0xFFFF | R/W | NV |  | 1 | 1 | ULong | LSR | Scale depends on CT size. See H8036 Modbus Integer Conversion tab.
|  |  | Real Energy Consumption (redundant) |  |  |  | 0-0xFFFF |  |  |  | 2 | 1 |  | MSR
|  |  | Total Instantaneous Real Power (3 Phase Total) |  |  | kW | 0-32767 | R |  |  | 3 | 1 | UInt
|  |  | Total Instantaneous Reactive Power (3 Phase Total) |  |  | kVAR | 0-32767 | R |  |  | 4 | 1 | UInt
|  |  | Total Instantaneous Apparent Power (3 Phase Total) |  |  | kVA | 0-32767 | R |  |  | 5 | 1 | UInt
|  |  | Total Power Factor (Total KW / Total KVA) |  |  | Ratio | 0-32768 | R |  |  | 6 | 1 | UInt
|  |  | Voltage, Line to Line, Average of Phases |  |  | Volt | 0-32767 | R |  |  | 7 | 1 | UInt
|  |  | Voltage, Line to Neutral, Average of Phases |  |  | Volt | 0-32767 | R |  |  | 8 | 1 | UInt
|  |  | Current, Average of Phases |  |  | Amp | 0-32767 | R |  |  | 9 | 1 | UInt
|  |  | Real Power, Phase A |  |  | kW | 0-32767 | R |  |  | 10 | 1 | UInt
|  |  | Real Power, Phase B |  |  | kW | 0-32767 | R |  |  | 11 | 1 | UInt
|  |  | Real Power, Phase C |  |  | kW | 0-32767 | R |  |  | 12 | 1 | UInt
|  |  | Power Factor, Phase A |  |  | Ratio | 0-32768 | R |  |  | 13 | 1 | UInt
|  |  | Power Factor, Phase B |  |  | Ratio | 0-32768 | R |  |  | 14 | 1 | UInt
|  |  | Power Factor, Phase C |  |  | Ratio | 0-32768 | R |  |  | 15 | 1 | UInt
|  |  | Voltage, Phase A-B |  |  | Volt | 0-32767 | R |  |  | 16 | 1 | UInt
|  |  | Voltage, Phase B-C |  |  | Volt | 0-32767 | R |  |  | 17 | 1 | UInt
|  |  | Voltage, Phase A-C |  |  | Volt | 0-32767 | R |  |  | 18 | 1 | UInt
|  |  | Voltage, Phase A-N |  |  | Volt | 0-32767 | R |  |  | 19 | 1 | UInt
|  |  | Voltage, Phase B-N |  |  | Volt | 0-32767 | R |  |  | 20 | 1 | UInt
|  |  | Voltage, Phase C-N |  |  | Volt | 0-32767 | R |  |  | 21 | 1 | UInt
|  |  | Current, Instantaneous, Phase A |  |  | Amp | 0-32767 | R |  |  | 22 | 1 | UInt
|  |  | Current, Instantaneous, Phase B |  |  | Amp | 0-32767 | R |  |  | 23 | 1 | UInt
|  |  | Current, Instantaneous, Phase C |  |  | Amp | 0-32767 | R |  |  | 24 | 1 | UInt
|  |  | Present Demand Sub–Interval |  |  | kW | 0-32767 | R |  |  | 25 | 1 | UInt
|  |  | Minimum Demand |  |  | kW | 0-32767 | R | NV |  | 26 | 1 | UInt
|  |  | Maximum Demand |  |  | kW | 0-32767 | R | NV |  | 27 | 1 | UInt
|  |  | Present Demand |  |  | kW | 0-32767 | R | NV |  | 28 | 1 | UInt
|  |  | Peak Demand |  |  | kW | 0-32767 | R | NV |  | 29 | 1 | UInt
|  |  | Reserved, Returns 0x8000 (QNAN) |  |  |  | 0x8000 | R |  |  | 30 | 1 | UInt
|  |  | CT Size (100, 300, etc.) |  |  | Amps | 0-32767 | R | NV |  | 31 | 1 | UInt
|  |  | Count of kWH Resets |  |  | Count | 0-32767 | R | NV |  | 32 | 1 | UInt
|  |  | Count of Peak Demand Resets |  |  | Count | 0-32767 | R | NV |  | 33 | 1 | UInt
|  |  | Count of Sub Intervals |  |  | Count | 0-32767 | R | NV |  | 34 | 1 | UInt
|  |  | Count of Number Readings in Present Sub–Interval |  |  | Count | 0-32767 | R | NV |  | 35 | 1 | UInt
Enercept Configuration
|  | · | System Type: See Manual. | 20 = Single Phase, 2-Wire: A + N E2x/E5x: 10 20 = Single Phase, 2-Wire: A + B 21 = Single Split Phase, 3-Wire: A + B + N 30 = 3 Phase Delta, ∆, A + B + C, no N 40 = 3 Phase Wye, Y, A + B + C + N |  | integer | 20 21 30 40 | R/W | NV |  | 36 | 1 | UInt
|  | · | Sub–Interval Length: Sets the length of a sub–interval. Value is the number of seconds times 5 (for example, 15 minutes is 4500). For sync–to–comms, set this to zero. |  |  | integer | 0-32767 | R/W | NV |  | 37 | 1 | UInt
|  | · | Number of sub-intervals per demand interval. Sets the number of sub-intervals that make a single demand interval. Legal values are 1 to 6. For block demand, set this to 1. |  |  | integer | 1-6 | R/W | NV |  | 38 | 1 | UInt
| · | · | Command | bit 0 (mask 1) = Begin new demand sub-interval bit 1 (mask 2) = Clear kWH accumulator (only command supported on Basic model) bit 2 (mask 3) = Reset peak demand |  | bit map | 0x00 - 0x07 | R/W | NV |  | 39 | 1 | UInt
| · | · | Reserved, Returns 0x8000 (QNAN) |  |  |  | 0x8000 | R |  |  | 40 | 217 | UInt
Enercept Float Data | [10 empty] | 257 | 70
| · | · | Real Energy Consumption | Clear by writing a 0 to either integer kWh register #1 or 2. |  | kWh |  | R/W | NV |  | 257 | 2 | Float | 32 bit IEEE Standard 754 single precision floating point value encoded in two registers: MSW in low address, LSW in high address (257/258 = MSW/LSW).
| · | · | Real Energy Consumption (redundant) |  |  | kWh |  | R/W | NV |  | 259 | 2 | Float
| · | · | Total Instantaneous Real Power |  |  | kW |  | R |  |  | 261 | 2 | Float
|  | · | Total Instantaneous Reactive Power |  |  | kVAR |  | R |  |  | 263 | 2 | Float
|  | · | Total Instantaneous Apparent Power |  |  | kVA |  | R |  |  | 265 | 2 | Float
|  | · | Total Power Factor (Total KW / Total KVA) |  |  | Ratio | 0.0-1.0 | R |  |  | 267 | 2 | Float
|  | · | Voltage, Line to Line, Average of 3 Phases |  |  | Volt |  | R |  |  | 269 | 2 | Float
|  | · | Voltage, Line to Neutral, Average of 3 Phases |  |  | Volt |  | R |  |  | 271 | 2 | Float
|  | · | Current, Average of 3 Phases |  |  | Amp |  | R |  |  | 273 | 2 | Float
|  | · | Real Power, Phase A |  |  | kW |  | R |  |  | 275 | 2 | Float
|  | · | Real Power, Phase B |  |  | kW |  | R |  |  | 277 | 2 | Float
|  | · | Real Power, Phase C |  |  | kW |  | R |  |  | 279 | 2 | Float
|  | · | Power Factor, Phase A |  |  | Ratio | 0.0-1.0 | R |  |  | 281 | 2 | Float
|  | · | Power Factor, Phase B |  |  | Ratio | 0.0-1.0 | R |  |  | 283 | 2 | Float
|  | · | Power Factor, Phase C |  |  | Ratio | 0.0-1.0 | R |  |  | 285 | 2 | Float
|  | · | Voltage, Phase A-B |  |  | Volt |  | R |  |  | 287 | 2 | Float
|  | · | Voltage, Phase B-C |  |  | Volt |  | R |  |  | 289 | 2 | Float
|  | · | Voltage, Phase A-C |  |  | Volt |  | R |  |  | 291 | 2 | Float
|  | · | Voltage, Phase A-N |  |  | Volt |  | R |  |  | 293 | 2 | Float
|  | · | Voltage, Phase B-N |  |  | Volt |  | R |  |  | 295 | 2 | Float
|  | · | Voltage, Phase C-N |  |  | Volt |  | R |  |  | 297 | 2 | Float
|  | · | Current, Instantaneous, Phase A |  |  | Amp |  | R |  |  | 299 | 2 | Float
|  | · | Current, Instantaneous, Phase B |  |  | Amp |  | R |  |  | 301 | 2 | Float
|  | · | Current, Instantaneous, Phase C |  |  | Amp |  | R |  |  | 303 | 2 | Float
|  | · | Present Demand Sub–Interval |  |  | kW |  | R |  |  | 305 | 2 | Float
|  | · | Minimum Demand |  |  | kW |  | R | NV |  | 307 | 2 | Float
|  | · | Maximum Demand |  |  | kW |  | R | NV |  | 309 | 2 | Float
|  | · | Present Demand |  |  | kW |  | R | NV |  | 311 | 2 | Float
|  | · | Peak Demand |  |  | kW |  | R | NV |  | 313 | 2 | Float
|  | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  | 0x7FC00000 | R |  |  | 315 | 2
| · | · | CT Size (100, 300, etc.) |  |  | Amps |  | R | NV |  | 317 | 2 | Float
| · | · | Count of kWH Resets |  |  | Integer |  | R | NV |  | 319 | 2 | Float
|  | · | Count of Peak Demand Resets |  |  | Integer |  | R | NV |  | 321 | 2 | Float
|  | · | Count of Sub Intervals |  |  | Integer |  | R | NV |  | 323 | 2 | Float
|  | · | Count of Number Readings in Present Sub–Interval |  |  | Integer |  | R | NV |  | 325 | 2 | Float
| · | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  | 0x7FC00000 | R |  |  | 327 | 760 | Float
Uni-Directional Meter Data |  |  |  | Insensitive to CT orientation
Uni-Directional Integer Data | [10 empty] | 1025 | 67
Uni-Dir Integer - Summary | [10 empty] | 1025 | 27
| · | · | Real Energy Consumption (MSR) | Accumulated Real (Active) Energy (Ph) | Accumulated Energy: Reset via Command Register | kWh | 0-0xFFFF | R | NV |  | 1025 | 1 | ULong | MSR | E
| · | · | Real Energy Consumption (LSR) |  |  |  | 0-0xFFFF |  |  |  | 1026 | 1 |  | LSR
|  | · | Reactive Energy Consumption (MSR) | Accumulated Reactive Energy (Qh) |  | KVARh | 0-0xFFFF | R | NV |  | 1027 | 1 | ULong | MSR | E
|  | · | Reactive Energy Consumption (LSR) |  |  |  | 0-0xFFFF |  |  |  | 1028 | 1 |  | LSR
|  | · | Apparent Energy Consumption (MSR) | Accumulated Apparent Energy (Sh) |  | KVAh | 0-0xFFFF | R | NV |  | 1029 | 1 | ULong | MSR | E
|  | · | Apparent Energy Consumption (LSR) |  |  |  | 0-0xFFFF |  |  |  | 1030 | 1 |  | LSR
| · | · | Total Instantaneous Real (P) Power | Total Power | Instantaneous Values | kW | 0-32767 | R |  |  | 1031 | 1 | UInt |  | W
|  | · | Total Instantaneous Reactive (Q) Power |  |  | kVAR | 0-32767 | R |  |  | 1032 | 1 | UInt |  | W
|  | · | Total Instantaneous Apparent (S) Power |  |  | kVA | 0-32767 | R |  |  | 1033 | 1 | UInt |  | W
|  | · | Average Power Factor (PF: Total KW / Total KVA) | Average of Active Phases |  | Ratio | 0-10000 | R |  |  | 1034 | 1 | UInt |  | 0.0001
|  | · | Voltage - Line to Line (U), Average of Active Phases |  |  | Volt | 0-32767 | R |  |  | 1035 | 1 | UInt |  | V
|  | · | Voltage - Line to Neutral (V), Average of Active Phases |  |  | Volt | 0-32767 | R |  |  | 1036 | 1 | UInt |  | V
|  | · | Current, Average of Active Phases |  |  | Amp | 0-32767 | R |  |  | 1037 | 1 | UInt |  | I
|  | · | Frequency (derived from phase A, B, or C in that order) | Frequency |  | Hz | 4500-6500 | R |  |  | 1038 | 1 | UInt |  | 0.01
|  | · | Total Real Power Present Demand | Present | Demand | kW | 0-32767 | R |  |  | 1039 | 1 | UInt |  | W
|  | · | Total Reactive Power Present Demand |  |  | kVAR | 0-32767 | R |  |  | 1040 | 1 | UInt |  | W
|  | · | Total Apparent Power Present Demand |  |  | kVA | 0-32767 | R |  |  | 1041 | 1 | UInt |  | W
|  | · | Total Real Power Max Demand | Maximum |  | kW | 0-32767 | R | NV |  | 1042 | 1 | UInt |  | W
|  | · | Total Reactive Power Max Demand |  |  | kVAR | 0-32767 | R | NV |  | 1043 | 1 | UInt |  | W
|  | · | Total Apparent Power Max Demand |  |  | kVA | 0-32767 | R | NV |  | 1044 | 1 | UInt |  | W
|  | · | Reserved, Returns 0x8000 (QNAN) |  |  |  | 0x8000 | R |  |  | 1045 | 3 | UInt
|  | · | Pulse Counter 1 (Real Energy) | Contact Closure Counters. Valid for both Pulse inputs and outputs. Default count source are shown in (). Clear via Command Register. Inputs are user defined. Reset via Command Register |  | Counter | 0-0xFFFF | R | NV |  | 1048 | 1 | ULong | MSR
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1049 | 1 |  | LSR
|  | · | Pulse Counter 2 (Reactive Energy) |  |  | Counter | 0-0xFFFF | R | NV |  | 1050 | 1 | ULong | MSR
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1051 | 1 |  | LSR
|  | · | Reserved, Returns 0x8000 (QNAN) |  |  |  | 0x8000 | R |  |  | 1052 | 4 | UInt
Uni-Dir Integer - Per Phase | [10 empty] | 1056 | 40
|  | · | Real Energy Consumption, Phase A | Real (Active) Energy (Ph) | Accumulated Energy: Reset via Command Register | kWh | 0-0xFFFF | R | NV |  | 1056 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1057 | 1 |  | LSR
|  | · | Real Energy Consumption, Phase B |  |  | kWh | 0-0xFFFF | R | NV |  | 1058 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1059 | 1 |  | LSR
|  | · | Real Energy Consumption, Phase C |  |  | kWh | 0-0xFFFF | R | NV |  | 1060 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1061 | 1 |  | LSR
|  | · | Reactive Energy Consumption, Phase A | Reactive Energy (Qh) |  | kWh | 0-0xFFFF | R | NV |  | 1062 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1063 | 1 |  | LSR
|  | · | Reactive Energy Consumption, Phase B |  |  | kWh | 0-0xFFFF | R | NV |  | 1064 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1065 | 1 |  | LSR
|  | · | Reactive Energy Consumption, Phase C |  |  | kWh | 0-0xFFFF | R | NV |  | 1066 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1067 | 1 |  | LSR
|  | · | Apparent Energy Consumption, Phase A | Apparent Energy (Sh) |  | kWh | 0-0xFFFF | R | NV |  | 1068 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1069 | 1 |  | LSR
|  | · | Apparent Energy Consumption, Phase B |  |  | kWh | 0-0xFFFF | R | NV |  | 1070 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1071 | 1 |  | LSR
|  | · | Apparent Energy Consumption, Phase C |  |  | kWh | 0-0xFFFF | R | NV |  | 1072 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 1073 | 1 |  | LSR
|  | · | Real Power, Phase A | Real (Active) Power (P) | Instantaneous Values | kW | 0-32767 | R |  |  | 1074 | 1 | UInt |  | W
|  | · | Real Power, Phase B |  |  | kW | 0-32767 | R |  |  | 1075 | 1 | UInt |  | W
|  | · | Real Power, Phase C |  |  | kW | 0-32767 | R |  |  | 1076 | 1 | UInt |  | W
|  | · | Reactive Power, Phase A | Reactive Power (Q) |  | kVAR | 0-32767 | R |  |  | 1077 | 1 | UInt |  | W
|  | · | Reactive Power, Phase B |  |  | kVAR | 0-32767 | R |  |  | 1078 | 1 | UInt |  | W
|  | · | Reactive Power, Phase C |  |  | kVAR | 0-32767 | R |  |  | 1079 | 1 | UInt |  | W
|  | · | Apparent Power, Phase A | Apparent Power (S) |  | kVA | 0-32767 | R |  |  | 1080 | 1 | UInt |  | W
|  | · | Apparent Power, Phase B |  |  | kVA | 0-32767 | R |  |  | 1081 | 1 | UInt |  | W
|  | · | Apparent Power, Phase C |  |  | kVA | 0-32767 | R |  |  | 1082 | 1 | UInt |  | W
|  | · | Power Factor, Phase A | Power Factor |  | Ratio | 0-10000 | R |  |  | 1083 | 1 | UInt |  | 0.0001
|  | · | Power Factor, Phase B |  |  | Ratio | 0-10000 | R |  |  | 1084 | 1 | UInt |  | 0.0001
|  | · | Power Factor, Phase C |  |  | Ratio | 0-10000 | R |  |  | 1085 | 1 | UInt |  | 0.0001
|  | · | Voltage, Phase A-B | Voltage - Line to Line |  | Volt | 0-32767 | R |  |  | 1086 | 1 | UInt |  | V
|  | · | Voltage, Phase B-C |  |  | Volt | 0-32767 | R |  |  | 1087 | 1 | UInt |  | V
|  | · | Voltage, Phase A-C |  |  | Volt | 0-32767 | R |  |  | 1088 | 1 | UInt |  | V
|  | · | Voltage, Phase A-N | Voltage - Line to Neutral |  | Volt | 0-32767 | R |  |  | 1089 | 1 | UInt |  | V
|  | · | Voltage, Phase B-N |  |  | Volt | 0-32767 | R |  |  | 1090 | 1 | UInt |  | V
|  | · | Voltage, Phase C-N |  |  | Volt | 0-32767 | R |  |  | 1091 | 1 | UInt |  | V
|  | · | Current, Phase A | Current |  | Amp | 0-32767 | R |  |  | 1092 | 1 | UInt |  | I
|  | · | Current, Phase B |  |  | Amp | 0-32767 | R |  |  | 1093 | 1 | UInt |  | I
|  | · | Current, Phase C |  |  | Amp | 0-32767 | R |  |  | 1094 | 1 | UInt |  | I
|  | · | Current, Neutral |  |  | Amp | 0-32767 | R |  |  | 1095 | 1 | UInt |  | I
|  | · | Reserved, Returns 0x8000 (QNAN) |  |  | Amp | 0-32767 | R |  |  | 1096 | 12 | UInt
Uni-Directional Floating Point Data | [10 empty] | 1537 | 106
Uni-Dir Float – Summary | [10 empty] | 1537 | 44
| · | · | Real Energy (Ph) Consumption | Accumulated Energy: Reset via Command Register |  | kWh |  | R | NV |  | 1537 | 2 | Float
|  | · | Reactive Energy (Qh) Consumption |  |  | kVARh |  | R | NV |  | 1539 | 2 | Float
|  | · | Apparent Energy (Sh) Consumption |  |  | kVAh |  | R | NV |  | 1541 | 2 | Float
| · | · | Total Instantaneous Real Power (P) | Total of Active Phases | Instantaneous Values | kW |  | R |  |  | 1543 | 2 | Float
|  | · | Total Instantaneous Reactive Power (Q) |  |  | kVAR |  | R |  |  | 1545 | 2 | Float
|  | · | Total Instantaneous Apparent Power (S) |  |  | kVA |  | R |  |  | 1547 | 2 | Float
|  | · | Average Power Factor (PF: Total KW / Total KVA) | Average of Active Phases |  | Ratio | 0.0-1.0 | R |  |  | 1549 | 2 | Float
|  | · | Voltage Line to Line (U), Average of Active Phases |  |  | Volt |  | R |  |  | 1551 | 2 | Float
|  | · | VoltageLine to Neutral (V), Average of Active Phases |  |  | Volt |  | R |  |  | 1553 | 2 | Float
|  | · | Current, Average of Active Phases |  |  | Amp |  | R |  |  | 1555 | 2 | Float
|  | · | Frequency (derived from phase A, B, or C in that order) | Frequency |  | Hz | 45.0-65.0 | R |  |  | 1557 | 2 | Float
|  | · | Total Real Power Present Demand | Present | Demand | kW |  | R |  |  | 1559 | 2 | Float
|  | · | Total Reactive Power Present Demand |  |  | kVAR |  | R |  |  | 1561 | 2 | Float
|  | · | Total Apparent Power Present Demand |  |  | kVA |  | R |  |  | 1563 | 2 | Float
|  | · | Total Real Power Max Demand | Maximum |  | kW |  | R | NV |  | 1565 | 2 | Float
|  | · | Total Reactive Power Max Demand |  |  | kVAR |  | R | NV |  | 1567 | 2 | Float
|  | · | Total Apparent Power Max Demand |  |  | kVA |  | R | NV |  | 1569 | 2 | Float
|  | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  | 0x7FC00000 | R |  |  | 1571 | 6 | Float
|  | · | Pulse Counter 1 (Real Energy) | Contact Closure Counters. Valid for both Pulse inputs and outputs. Default counters are shown in (). Inputs are user defined. Reset via Command Register |  |  | 0 - 4294967040 | R |  |  | 1577 | 2 | Float |  | 1
|  | · | Pulse Counter 2 (Reactive Energy) |  |  |  | 0 - 4294967040 | R |  |  | 1579 | 2 | Float |  | 1
|  | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  | 0x7FC00000 | R |  |  | 1581 | 8 | Float
Uni-Dir Float – Per Phase | [10 empty] | 1589 | 62
|  | · | Real Energy Consumption, Phase A | Per Phase Real Energy (Ph) | Accumulated Energy Per Phase: Reset via Command Register | kWh |  | R | NV |  | 1589 | 2 | Float
|  | · | Real Energy Consumption, Phase B |  |  | kWh |  | R | NV |  | 1591 | 2 | Float
|  | · | Real Energy Consumption, Phase C |  |  | kWh |  | R | NV |  | 1593 | 2 | Float
|  | · | Reactive Energy Consumption, Phase A | Per Phase Reactive Energy (Qh) |  | kWh |  | R | NV |  | 1595 | 2 | Float
|  | · | Reactive Energy Consumption, Phase B |  |  | kWh |  | R | NV |  | 1597 | 2 | Float
|  | · | Reactive Energy Consumption, Phase C |  |  | kWh |  | R | NV |  | 1599 | 2 | Float
|  | · | Apparent Energy Consumption, Phase A | Per Phase Apparent Energy (Sh) |  | kWh |  | R | NV |  | 1601 | 2 | Float
|  | · | Apparent Energy Consumption, Phase B |  |  | kWh |  | R | NV |  | 1603 | 2 | Float
|  | · | Apparent Energy Consumption, Phase C |  |  | kWh |  | R | NV |  | 1605 | 2 | Float
|  | · | Real Power, Phase A | Real (Active) Power (P) | Instantaneous Values - Per Phase | kW |  | R |  |  | 1607 | 2 | Float
|  | · | Real Power, Phase B |  |  | kW |  | R |  |  | 1609 | 2 | Float
|  | · | Real Power, Phase C |  |  | kW |  | R |  |  | 1611 | 2 | Float
|  | · | Reactive Power, Phase A | Reactive Power (Q) |  | kVAR |  | R |  |  | 1613 | 2 | Float
|  | · | Reactive Power, Phase B |  |  | kVAR |  | R |  |  | 1615 | 2 | Float
|  | · | Reactive Power, Phase C |  |  | kVAR |  | R |  |  | 1617 | 2 | Float
|  | · | Apparent Power, Phase A | Apparent Power (S) |  | kVA |  | R |  |  | 1619 | 2 | Float
|  | · | Apparent Power, Phase B |  |  | kVA |  | R |  |  | 1621 | 2 | Float
|  | · | Apparent Power, Phase C |  |  | kVA |  | R |  |  | 1623 | 2 | Float
|  | · | Power Factor, Phase A | Power Factor (PF) |  | Ratio | 0.0-1.0 | R |  |  | 1625 | 2 | Float
|  | · | Power Factor, Phase B |  |  | Ratio | 0.0-1.0 | R |  |  | 1627 | 2 | Float
|  | · | Power Factor, Phase C |  |  | Ratio | 0.0-1.0 | R |  |  | 1629 | 2 | Float
|  | · | Voltage, Phase A-B | Voltage - Line to Line (U) |  | Volt |  | R |  |  | 1631 | 2 | Float
|  | · | Voltage, Phase B-C |  |  | Volt |  | R |  |  | 1633 | 2 | Float
|  | · | Voltage, Phase A-C |  |  | Volt |  | R |  |  | 1635 | 2 | Float
|  | · | Voltage, Phase A-N | Voltage - Line to Neutral (V) |  | Volt |  | R |  |  | 1637 | 2 | Float
|  | · | Voltage, Phase B-N |  |  | Volt |  | R |  |  | 1639 | 2 | Float
|  | · | Voltage, Phase C-N |  |  | Volt |  | R |  |  | 1641 | 2 | Float
|  | · | Current, Phase A | Current |  | Amp |  | R |  |  | 1643 | 2 | Float
|  | · | Current, Phase B |  |  | Amp |  | R |  |  | 1645 | 2 | Float
|  | · | Current, Phase C |  |  | Amp |  | R |  |  | 1647 | 2 | Float
|  | · | Current, Neutral |  |  | Amp |  | R |  |  | 1649 | 2 | Float
|  | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  | 0x7FC00000 | R | NV |  | 1651 | 24 | Float
Bi-Directional Meter Data |  |  |  | Sensitive to CT orientation
Bi-Directional Integer Data | [10 empty] | 2049 | 111
Bi-Dir Integer - Summary | [10 empty] | 2049 | 42
|  | · | Real Energy: Net (Import - Export) | Accumulated Real Energy | Accumulators: Clear via command register (see configuration register block) | kWh | 0-0xFFFF | R | NV |  | 2049 | 1 | SLong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2050 | 1 |  | LSR
|  | · | Real Energy: Quadrants 1 & 4 Import, Delivered, Down Stream |  |  | kWh | 0-0xFFFF | R | NV |  | 2051 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2052 | 1 |  | LSR
|  | · | Real Energy: Quadrants 2 & 3 Export, Received, Up Stream |  |  | kWh | 0-0xFFFF | R | NV |  | 2053 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2054 | 1 |  | LSR
|  | · | Reactive Energy – Quadrant 1: Inductive (IEEE), Lags Import Real Energy (IEC) | Accumulated Reactive Energy: Quadrants 3 + 4 = Export/Received Quadrants 1 + 2 = Import/Delivered |  | KVARh | 0-0xFFFF | R | NV |  | 2055 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2056 | 1 |  | LSR
|  | · | Reactive Energy – Quadrant 2: Inductive (IEEE), Leads Export Real Energy (IEC) |  |  | KVARh | 0-0xFFFF | R | NV |  | 2057 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2058 | 1 |  | LSR
|  | · | Reactive Energy – Quadrant 3: Capacitive (IEEE), Lags Export Real Energy (IEC) |  |  | KVARh | 0-0xFFFF | R | NV |  | 2059 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2060 | 1 |  | LSR
|  | · | Reactive Energy – Quadrant 4: Capacitive (IEEE), Leads Import Real Energy (IEC) |  |  | KVARh | 0-0xFFFF | R | NV |  | 2061 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2062 | 1 |  | LSR
|  | · | Apparent Energy: Net (Import - Export) | Accumulated Apparent Energy: Import and Export Correspond with Real Energy. Calculated as a vector sum. |  | KVAh | 0-0xFFFF | R | NV |  | 2063 | 1 | SLong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2064 | 1 |  | LSR
|  | · | Apparent Energy: Quadrants 1 & 4 Import, Delivered, Down Stream |  |  | KVAh | 0-0xFFFF | R | NV |  | 2065 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2066 | 1 |  | LSR
|  | · | Apparent Energy: Quadrants 2 & 3 Export, Received, Up Stream |  |  | KVAh | 0-0xFFFF | R | NV |  | 2067 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2068 | 1 |  | LSR
|  | · | Total Net Instantaneous Real (P) Power | Power | Instantaneous Values, Summary of Active Phases | kW | 0-32767 | R |  |  | 2069 | 1 | SInt |  | W
|  | · | Total Net Instantaneous Reactive (Q) Power |  |  | kVAR | 0-32767 | R |  |  | 2070 | 1 | SInt |  | W
|  | · | Total Net Instantaneous Apparent (S) Power (vector sum) |  |  | kVA | 0-32767 | R |  |  | 2071 | 1 | UInt |  | W
|  | · | Total Power Factor (Total KW / Total KVA) | PF |  | Ratio | 0-10000 | R |  |  | 2072 | 1 | SInt |  | 0.0001
|  | · | Voltage, L-L (U), Average of Active Phases | Voltage |  | Volt | 0-32767 | R |  |  | 2073 | 1 | UInt |  | V
|  | · | Voltage, L-N (V), Average of Active Phases |  |  | Volt | 0-32767 | R |  |  | 2074 | 1 | UInt |  | V
|  | · | Current, Average of Active Phases | Current |  | Amp | 0-32767 | R |  |  | 2075 | 1 | UInt |  | I
|  | · | Frequency | F |  | Hz | 4500-6500 | R |  |  | 2076 | 1 | UInt |  | 0.01
|  | · | Total Real Power Present Demand | Present | Demand | kW | 0-32767 | R |  |  | 2077 | 1 | SInt |  | W
|  | · | Total Reactive Power Present Demand |  |  | kVAR | 0-32767 | R |  |  | 2078 | 1 | SInt |  | W
|  | · | Total Apparent Power Present Demand |  |  | kVA | 0-32767 | R |  |  | 2079 | 1 | SInt |  | W
|  | · | Total Real Power Max Demand | Maximum: Import / Consume / Down Stream |  | kW | 0-32767 | R | NV |  | 2080 | 1 | SInt |  | W
|  | · | Total Reactive Power Max Demand |  |  | kVAR | 0-32767 | R | NV |  | 2081 | 1 | SInt |  | W
|  | · | Total Apparent Power Max Demand |  |  | kVA | 0-32767 | R | NV |  | 2082 | 1 | SInt |  | W
|  | · | Total Real Power Max Demand | Maximum: Export / Source / Up Stream |  | kW | 0-32767 | R | NV |  | 2083 | 1 | SInt |  | W
|  | · | Total Reactive Power Max Demand |  |  | kVAR | 0-32767 | R | NV |  | 2084 | 1 | SInt |  | W
|  | · | Total Apparent Power Max Demand |  |  | kVA | 0-32767 | R | NV |  | 2085 | 1 | SInt |  | W
|  | · | Reserved, Returns 0x8000 (QNAN) |  |  |  |  | R |  |  | 2086 | 1 | UInt
|  | · | Pulse Counter 1 (Import Real Energy) | Contact Closure Counters. Valid for both Pulse inputs and outputs. E21Cx counts are shown in (). See Energy per Pulse Configuration register for the Wh per pulse count. Clear via reset register. Inputs are user defined. |  |  | 0-0xFFFF | R | NV |  | 2087 | 1 | ULong | MSR
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2088 | 1 |  | LSR
|  | · | Pulse Counter 2 (Export Real Energy) |  |  |  | 0-0xFFFF | R | NV |  | 2089 | 1 | ULong | MSR
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2090 | 1 |  | LSR
Bi-Dir Integer - Per Phase | [10 empty] | 2091 | 69
|  | · | Accumulated Real Energy, Phase A | Import / Consume / Down Stream | Accumulated Real Energy (Ph), Per Phase | kWh | 0-0xFFFF | R | NV |  | 2091 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2092 | 1 |  | LSR
|  | · | Accumulated Real Energy, Phase B |  |  | kWh | 0-0xFFFF | R | NV |  | 2093 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2094 | 1 |  | LSR
|  | · | Accumulated Real Energy, Phase C |  |  | kWh | 0-0xFFFF | R | NV |  | 2095 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2096 | 1 |  | LSR
|  | · | Accumulated Real Energy, Phase A | Export / Source / Up Stream |  | kWh | 0-0xFFFF | R | NV |  | 2097 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2098 | 1 |  | LSR
|  | · | Accumulated Real Energy, Phase B |  |  | kWh | 0-0xFFFF | R | NV |  | 2099 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2100 | 1 |  | LSR
|  | · | Accumulated Real Energy, Phase C |  |  | kWh | 0-0xFFFF | R | NV |  | 2101 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2102 | 1 |  | LSR
|  | · | Accumulated Q1 Reactive Energy, Phase A | Import / Consume / Down Stream | Accumulated Reactive (Qh) Energy, Per Phase | kVARh | 0-0xFFFF | R | NV |  | 2103 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2104 | 1 |  | LSR
|  | · | Accumulated Q1 Reactive Energy, Phase B |  |  | kVARh | 0-0xFFFF | R | NV |  | 2105 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2106 | 1 |  | LSR
|  | · | Accumulated Q1 Reactive Energy, Phase C |  |  | kVARh | 0-0xFFFF | R | NV |  | 2107 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2108 | 1 |  | LSR
|  | · | Accumulated Q2 Reactive Energy, Phase A |  |  | kVARh | 0-0xFFFF | R | NV |  | 2109 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2110 | 1 |  | LSR
|  | · | Accumulated Q2 Reactive Energy, Phase B |  |  | kVARh | 0-0xFFFF | R | NV |  | 2111 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2112 | 1 |  | LSR
|  | · | Accumulated Q2 Reactive Energy, Phase C |  |  | kVARh | 0-0xFFFF | R | NV |  | 2113 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2114 | 1 |  | LSR
|  | · | Accumulated Q3 Reactive Energy, Phase A | Export / Source / Up Stream |  | kVARh | 0-0xFFFF | R | NV |  | 2115 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2116 | 1 |  | LSR
|  | · | Accumulated Q3 Reactive Energy, Phase B |  |  | kVARh | 0-0xFFFF | R | NV |  | 2117 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2118 | 1 |  | LSR
|  | · | Accumulated Q3 Reactive Energy, Phase C |  |  | kVARh | 0-0xFFFF | R | NV |  | 2119 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2120 | 1 |  | LSR
|  | · | Accumulated Q4 Reactive Energy, Phase A |  |  | kVARh | 0-0xFFFF | R | NV |  | 2121 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2122 | 1 |  | LSR
|  | · | Accumulated Q4 Reactive Energy, Phase B |  |  | kVARh | 0-0xFFFF | R | NV |  | 2123 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2124 | 1 |  | LSR
|  | · | Accumulated Q4 Reactive Energy, Phase C |  |  | kVARh | 0-0xFFFF | R | NV |  | 2125 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2126 | 1 |  | LSR
|  | · | Accumulated Apparent Energy, Phase A | Import / Consume / Down Stream | Accumulated Apparent (Sh) Energy, Per Phase | kVAh | 0-0xFFFF | R | NV |  | 2127 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2128 | 1 |  | LSR
|  | · | Accumulated Apparent Energy, Phase B |  |  | kVAh | 0-0xFFFF | R | NV |  | 2129 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2130 | 1 |  | LSR
|  | · | Accumulated Apparent Energy, Phase C |  |  | kVAh | 0-0xFFFF | R | NV |  | 2131 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2132 | 1 |  | LSR
|  | · | Accumulated Apparent Energy, Phase A | Export / Source / Up Stream |  | kVAh | 0-0xFFFF | R | NV |  | 2133 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2134 | 1 |  | LSR
|  | · | Accumulated Apparent Energy, Phase B |  |  | kVAh | 0-0xFFFF | R | NV |  | 2135 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2136 | 1 |  | LSR
|  | · | Accumulated Apparent Energy, Phase C |  |  | kVAh | 0-0xFFFF | R | NV |  | 2137 | 1 | ULong | MSR | E
|  | · |  |  |  |  | 0-0xFFFF |  |  |  | 2138 | 1 |  | LSR
|  | · | Real Power (P), Phase A | Real Power (P) | Instantaneous Values, Per Phase | kW | 0-32767 | R |  |  | 2139 | 1 | SInt |  | W
|  | · | Real Power (P), Phase B |  |  | kW | 0-32767 | R |  |  | 2140 | 1 | SInt |  | W
|  | · | Real Power (P), Phase C |  |  | kW | 0-32767 | R |  |  | 2141 | 1 | SInt |  | W
|  | · | Reactive Power (Q), Phase A | Reactive Power (Q) |  | kVAR | 0-32767 | R |  |  | 2142 | 1 | SInt |  | W
|  | · | Reactive Power (Q), Phase B |  |  | kVAR | 0-32767 | R |  |  | 2143 | 1 | SInt |  | W
|  | · | Reactive Power (Q), Phase C |  |  | kVAR | 0-32767 | R |  |  | 2144 | 1 | SInt |  | W
|  | · | Apparent Power (S), Phase A | Apparent Power (S) |  | kVA | 0-32767 | R |  |  | 2145 | 1 | UInt |  | W
|  | · | Apparent Power (S), Phase B |  |  | kVA | 0-32767 | R |  |  | 2146 | 1 | UInt |  | W
|  | · | Apparent Power (S), Phase C |  |  | kVA | 0-32767 | R |  |  | 2147 | 1 | UInt |  | W
|  | · | Power Factor (PF), Phase A | Power Factor (PF) |  | Ratio | 0-10000 | R |  |  | 2148 | 1 | SInt |  | 0.0001
|  | · | Power Factor (PF), Phase B |  |  | Ratio | 0-10000 | R |  |  | 2149 | 1 | SInt |  | 0.0001
|  | · | Power Factor (PF), Phase C |  |  | Ratio | 0-10000 | R |  |  | 2150 | 1 | SInt |  | 0.0001
|  | · | Voltage (U), Phase A-B | Voltage - Line to Line (U) |  | Volt | 0-32767 | R |  |  | 2151 | 1 | UInt |  | V
|  | · | Voltage (U), Phase B-C |  |  | Volt | 0-32767 | R |  |  | 2152 | 1 | UInt |  | V
|  | · | Voltage (U), Phase A-C |  |  | Volt | 0-32767 | R |  |  | 2153 | 1 | UInt |  | V
|  | · | Voltage (V), Phase A-N | Voltage - Line to Neutral (V) |  | Volt | 0-32767 | R |  |  | 2154 | 1 | UInt |  | V
|  | · | Voltage (V), Phase B-N |  |  | Volt | 0-32767 | R |  |  | 2155 | 1 | UInt |  | V
|  | · | Voltage (V), Phase C-N |  |  | Volt | 0-32767 | R |  |  | 2156 | 1 | UInt |  | V
|  | · | Current, Phase A | Current |  | Amp | 0-32767 | R |  |  | 2157 | 1 | UInt |  | I
|  | · | Current, Phase B |  |  | Amp | 0-32767 | R |  |  | 2158 | 1 | UInt |  | I
|  | · | Current, Phase C |  |  | Amp | 0-32767 | R |  |  | 2159 | 1 | UInt |  | I
|  | · | Current, Neutral |  |  | Amp | 0-32767 | R |  |  | 2160 | 1 | UInt |  | I
|  | · | Reserved, Reports QNAN (0x8000) |  |  |  | 0x8000 | R |  |  | 2161 | 12 | UInt
Bi-Directional Floating Point Data | [10 empty] | 2561 | 152
Bi-Dir Float - Summary | [10 empty] | 2561 | 60
|  | · | Accumulated Real Energy: Net (Import - Export) | Accumulated Real Energy | clear via command register | kWh |  | R | NV |  | 2561 | 2 | Float
|  | · | Real Energy: Quadrants 1 & 4 Import, Delivered, Down Stream |  |  | kWh |  | R | NV |  | 2563 | 2 | Float
|  | · | Real Energy: Quadrants 2 & 3 Export, Received, Up Stream |  |  | kWh |  | R | NV |  | 2565 | 2 | Float
|  | · | Reactive Energy – Quadrant 1: Lags Import Real Energy (IEC) Inductive (IEEE) | Accumulated Reactive Energy: Quadrants 1 + 2 = Import/Delivered Quadrants 3 + 4 = Export/Received |  | kVARh |  | R | NV |  | 2567 | 2 | Float
|  | · | Reactive Energy – Quadrant 2: Leads Export Real Energy (IEC) Inductive (IEEE) |  |  | kVARh |  | R | NV |  | 2569 | 2 | Float
|  | · | Reactive Energy – Quadrant 3: Lags Export Real Energy (IEC) Capacitive (IEEE) |  |  | kVARh |  | R | NV |  | 2571 | 2 | Float
|  | · | Reactive Energy – Quadrant 4: Leads Import Real Energy (IEC) Capacitive (IEEE) |  |  | kVARh |  | R | NV |  | 2573 | 2 | Float
|  | · | Apparent Energy: Net (Import - Export) | Accumulated Apparent Energy: Import and Export Correspond with Real Energy. Calculated as a vector sum. |  | kVAh |  | R | NV |  | 2575 | 2 | Float
|  | · | Apparent Energy: Quadrants 1 & 4 Import, Delivered, Down Stream |  |  | kVAh |  | R | NV |  | 2577 | 2 | Float
|  | · | Apparent Energy: Quadrants 2 & 3 Export, Received, Up Stream |  |  | kVAh |  | R | NV |  | 2579 | 2 | Float
|  | · | Total Net Instantaneous Real (P) Power | Power | Instantaneous Values, Summary of Active Phases | kW |  | R |  |  | 2581 | 2 | Float
|  | · | Total Net Instantaneous Reactive (Q) Power |  |  | kVAR |  | R |  |  | 2583 | 2 | Float
|  | · | Total Net Instantaneous Apparent (S) Power (vector sum) |  |  | kVA |  | R |  |  | 2585 | 2 | Float
|  | · | Total Power Factor (Total KW / Total KVA) | PF |  | Ratio | 0.0-1.0 | R |  |  | 2587 | 2 | Float
|  | · | Voltage, L-L (U), Average of Active Phases | Voltage |  | Volt |  | R |  |  | 2589 | 2 | Float
|  | · | Voltage, L-N (V), Average of Active Phases |  |  | Volt |  | R |  |  | 2591 | 2 | Float
|  | · | Current, Average of Active Phases | Current |  | Amp |  | R |  |  | 2593 | 2 | Float
|  | · | Frequency | F |  | Hz | 45.0-65.0 | R |  |  | 2595 | 2 | Float
|  | · | Total Real Power Present Demand | Present | Demand | kW |  | R |  |  | 2597 | 2 | Float
|  | · | Total Reactive Power Present Demand |  |  | kVAR |  | R |  |  | 2599 | 2 | Float
|  | · | Total Apparent Power Present Demand |  |  | kVA |  | R |  |  | 2601 | 2 | Float
|  | · | Total Real Power Max Demand | Maximum: Import / Consume / Down Stream |  | kW |  | R | NV |  | 2603 | 2 | Float
|  | · | Total Reactive Power Max Demand |  |  | kVAR |  | R | NV |  | 2605 | 2 | Float
|  | · | Total Apparent Power Max Demand |  |  | kVA |  | R | NV |  | 2607 | 2 | Float
|  | · | Total Real Power Max Demand | Maximum: Export / Source / Up Stream |  | kW |  | R | NV |  | 2609 | 2 | Float
|  | · | Total Reactive Power Max Demand |  |  | kVAR |  | R | NV |  | 2611 | 2 | Float
|  | · | Total Apparent Power Max Demand |  |  | kVA |  | R | NV |  | 2613 | 2 | Float
|  | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  |  | R |  |  | 2615 | 2 | Float
|  | · | Pulse Counter 1 (Import Real Energy) | Contact Closure Counters. Valid for both Pulse inputs and outputs. E21Cx counts are shown in (). See register 144 – Energy per Pulse for the Wh per pulse count. Clear via command register. Inputs are user defined. These values are derived from the 32 bit integer counter and will roll over to 0 when the integer counters do. |  |  | 0 - 4294967040 | R |  |  | 2617 | 2 | Float |  | 1
|  | · | Pulse Counter 2 (Export Real Energy) |  |  |  | 0 - 4294967040 | R |  |  | 2619 | 2 | Float |  | 1
Bi-Dir Float – Per Phase | [10 empty] | 2621 | 92
|  | · | Accumulated Real Energy, Phase A | Import / Consume / Down Stream | Accumulated Real (Ph) Energy | kWh |  | R |  |  | 2621 | 2 | Float
|  | · | Accumulated Real Energy, Phase B |  |  | kWh |  | R |  |  | 2623 | 2 | Float
|  | · | Accumulated Real Energy, Phase C |  |  | kWh |  | R |  |  | 2625 | 2 | Float
|  | · | Accumulated Real Energy, Phase A | Export / Source / Up Stream |  | kWh |  | R |  |  | 2627 | 2 | Float
|  | · | Accumulated Real Energy, Phase B |  |  | kWh |  | R |  |  | 2629 | 2 | Float
|  | · | Accumulated Real Energy, Phase C |  |  | kWh |  | R |  |  | 2631 | 2 | Float
|  | · | Accumulated Q1 Reactive Energy, Phase A | Quadrant 1: Import / Consume / Down Stream | Accumulated Reactive (Qh) Energy | kVARh |  | R |  |  | 2633 | 2 | Float
|  | · | Accumulated Q1 Reactive Energy, Phase B |  |  | kVARh |  | R |  |  | 2635 | 2 | Float
|  | · | Accumulated Q1 Reactive Energy, Phase C |  |  | kVARh |  | R |  |  | 2637 | 2 | Float
|  | · | Accumulated Q2 Reactive Energy, Phase A | Quadrant 2: Import / Consume / Down Stream |  | kVARh |  | R |  |  | 2639 | 2 | Float
|  | · | Accumulated Q2 Reactive Energy, Phase B |  |  | kVARh |  | R |  |  | 2641 | 2 | Float
|  | · | Accumulated Q2 Reactive Energy, Phase C |  |  | kVARh |  | R |  |  | 2643 | 2 | Float
|  | · | Accumulated Q3 Reactive Energy, Phase A | Quadrant 3: Export / Source / Up Stream |  | kVARh |  | R |  |  | 2645 | 2 | Float
|  | · | Accumulated Q3 Reactive Energy, Phase B |  |  | kVARh |  | R |  |  | 2647 | 2 | Float
|  | · | Accumulated Q3 Reactive Energy, Phase C |  |  | kVARh |  | R |  |  | 2649 | 2 | Float
|  | · | Accumulated Q4 Reactive Energy, Phase A | Quadrant 4: Export / Source / Up Stream |  | kVARh |  | R |  |  | 2651 | 2 | Float
|  | · | Accumulated Q4 Reactive Energy, Phase B |  |  | kVARh |  | R |  |  | 2653 | 2 | Float
|  | · | Accumulated Q4 Reactive Energy, Phase C |  |  | kVARh |  | R |  |  | 2655 | 2 | Float
|  | · | Accumulated Apparent Energy, Phase A | Import / Consume / Down Stream | Accumulated Apparent (Sh) Energy | kVAh |  | R |  |  | 2657 | 2 | Float
|  | · | Accumulated Apparent Energy, Phase B |  |  | kVAh |  | R |  |  | 2659 | 2 | Float
|  | · | Accumulated Apparent Energy, Phase C |  |  | kVAh |  | R |  |  | 2661 | 2 | Float
|  | · | Accumulated Apparent Energy, Phase A | Export / Source / Up Stream |  | kVAh |  | R |  |  | 2663 | 2 | Float
|  | · | Accumulated Apparent Energy, Phase B |  |  | kVAh |  | R |  |  | 2665 | 2 | Float
|  | · | Accumulated Apparent Energy, Phase C |  |  | kVAh |  | R |  |  | 2667 | 2 | Float
|  | · | Real Power, Phase A |  | Real Power (P) | kW |  | R |  |  | 2669 | 2 | Float
|  | · | Real Power, Phase B |  |  | kW |  | R |  |  | 2671 | 2 | Float
|  | · | Real Power, Phase C |  |  | kW |  | R |  |  | 2673 | 2 | Float
|  | · | Reactive Power, Phase A |  | Reactive Power (Q) | kVAR |  | R |  |  | 2675 | 2 | Float
|  | · | Reactive Power, Phase B |  |  | kVAR |  | R |  |  | 2677 | 2 | Float
|  | · | Reactive Power, Phase C |  |  | kVAR |  | R |  |  | 2679 | 2 | Float
|  | · | Apparent Power, Phase A |  | Apparent Power (S) | kVA |  | R |  |  | 2681 | 2 | Float
|  | · | Apparent Power, Phase B |  |  | kVA |  | R |  |  | 2683 | 2 | Float
|  | · | Apparent Power, Phase C |  |  | kVA |  | R |  |  | 2685 | 2 | Float
|  | · | Power Factor, Phase A |  | Power Factor (PF) | Ratio | 0.0-1.0 | R |  |  | 2687 | 2 | Float
|  | · | Power Factor, Phase B |  |  | Ratio | 0.0-1.0 | R |  |  | 2689 | 2 | Float
|  | · | Power Factor, Phase C |  |  | Ratio | 0.0-1.0 | R |  |  | 2691 | 2 | Float
|  | · | Voltage, Phase A-B |  | Line to Line Voltage (U) | Volt |  | R |  |  | 2693 | 2 | Float
|  | · | Voltage, Phase B-C |  |  | Volt |  | R |  |  | 2695 | 2 | Float
|  | · | Voltage, Phase A-C |  |  | Volt |  | R |  |  | 2697 | 2 | Float
|  | · | Voltage, Phase A-N |  | Line to Neutral Voltage (V) | Volt |  | R |  |  | 2699 | 2 | Float
|  | · | Voltage, Phase B-N |  |  | Volt |  | R |  |  | 2701 | 2 | Float
|  | · | Voltage, Phase C-N |  |  | Volt |  | R |  |  | 2703 | 2 | Float
|  | · | Current, Phase A |  | Current | Amp |  | R |  |  | 2705 | 2 | Float
|  | · | Current, Phase B |  |  | Amp |  | R |  |  | 2707 | 2 | Float
|  | · | Current, Phase C |  |  | Amp |  | R |  |  | 2709 | 2 | Float
|  | · | Current, Neutral (measured or calculated) |  |  | Amp |  | R |  |  | 2711 | 2 | Float
|  | · | Reserved, Reports QNAN (0x7FC00000) |  |  |  | 0x7FC00000 | R |  |  | 2713 | 24 | Float
Meter Configuration & Logging
Configuration - Meter |  |  | Note: W indicates a register that is Writable on Universal models, but is Read Only on System Calibrated models. If meter is Locked via Mode Rotary, writes are limited. | [7 empty] | 4171 | 37
| · | · | Calibration Event Counter. Security feature. Increments whenever the meter Calibration is successfully written. |  |  | count | 0-32767 | R | NV |  | 4171 | 1 | UInt
| · | · | Configuration Event Counter. Security feature.Increments whenever the meter configuration is successfully written. |  |  | count | 0-32767 | R | NV |  | 4172 | 1 | UInt
| · | · | Analog Output Mode: Output not supported on all models. The mode select the units and the reference for 100% of full scale. 0 = Not Supported on this model. 1 = Watts. Full scale set by the Theoretical Maximum System Power calculated by the meter below. 2 = VAR. Full scale set by the Theoretical Maximum System Power calculated by the meter below. 3 = Amps. Average of active phases set by System Type set below. Full scale set by the CT Primary size below. 4 = Volts. Average of active phases set by System Type set below. Full scale set by the System Voltage below. |  |  | integer | 0 - 4 | R/W | NV |  | 4173 | 1 | UInt
| · | · | CT Input Polarity Bit Map: Controls the polarity of the input signal from the CT. Has 4 bits for CTs ABCN. If a bit is 0, the associated CT current data polarity is unchanged (the default). If the bit is set to 1, polarity of the CT data is inverted. Setting a bit to 1 has the effect of taking the CT off the wire, flipping it over, and putting it back on the wire, changing the direction of the to load arrow. Bit 0 is CT N, Bit 1 is phase A (L1), bit 2 is B (L2), bit 3 is C (L3). Default is 0x0000. Bit 0: Neutral CT Bit 1: CT L1 (A) Bit 2: CT L2 (B) Bit 3: CT L3 (C) Bits 4 - 15: unused |  |  | Bitmap | 0-0x000F | R/W | NV |  | 4174 | 1 | UInt
| · | · | Voltage Input L1 (A) to CT Input Association: Default is 1. | Voltage to Current Input Association: Controls which CT input each voltage input is convoluted with to calculate real, reactive, and apparent power. |  | integer | 1 - 4 | R/W | NV |  | 4175 | 1 | UInt
| · | · | Voltage Input L2 (B) to CT Input Association: Default is 2. |  |  | integer | 1 - 4 | R/W | NV |  | 4176 | 1 | UInt
| · | · | Voltage Input L3 (B) to CT Input Association: Default is 3. |  |  | integer | 1 - 4 | R/W | NV |  | 4177 | 1 | UInt
| · | · | Meter Control Override Bitmap: 1 = Active. Indicates if any of the physical rotary controls on the meter have been overridden via communications. If the associated bit is True (1), the value that the control indicates is not correct, the value written over comms is being used by the meter. If any bit bit in this register is true, the Overrride LED on the meter is illuminated. Bit 0: CT Primary Size Control Overridden. Bit 1: Energy Pulse Weight Control Overridden. Bit 2: Device Address (Modbus RTU or BACnet MS/TP) Control Overridden. Bit 3: Meter Mode Control Overridden. Bit 4: Analog Output Control Overridden. Bit 5: CT Interface Overridden (Voltage Mode vs Rogowski CT). Bits 6-7: Reserved, return 0. Bits 4 – 7: Reserved, return 0. Bits 8 - 11: Reserved, return 0. Bits12 – 15: Reserved, return 0. |  |  | Bitmap | 0-0xFFFF | R | NV |  | 4178 | 1 | UInt
| · | · | Command Register: - Write 30078 (0x757E) to clear all Energy Accumulators to 0 (All). - Write 21212 (0x52DC) to reset Max Demand values to Present Demand Values. Takes effect at the end of the next 1 second calculation cycle. Write no more frequently than every 10 seconds. Not available on BDS models. - Write 21211 (0x52DB) to begin new Demand Sub-Interval calculation cycle. Only supported when demand is in sync-to-comms mode (Number of Demand Sub-Intervals is set to 0). Takes effect at the end of the next 1 second calculation cycle. Write no more frequently than every 10 seconds. Not available on BDS models. - Write 16640 (0x4100) to Reset Logging. Logging models only. - Write 16498 (0x4072) to Clear Pulse Counters to 0. - Write 12345 (0x3039) to reset all Min/Max values to present values. EDS models only. - Read always returns 0. |  |  | integer | N/A | R/W |  |  | 4179 | 1 | UInt
| · | · | System Type: See Manual. Note: only the indicated phases are monitored for Phase Loss. | Single Phase: A + N Single Phase: A + B Single Split Phase: A + B + N 3 phase ∆, A + B + C, no N 3 phase Y, A + B + C + N |  |  | 10 11 12 31 40 | R/W | NV |  | 4180 | 1 | UInt
| · | · | CT Primary: 1-12800 = CT Current Rating for phase A, B, & C. Not configurable on system calibrated models. |  | CT Ratio Configuration | Amps | 1-12800 | R/W | NV |  | 4181 | 1 | UInt
| · | · | Current Input / CT Secondary Bitmap: 1 = Active. Not user configurable on System Calibrated models. Either Voltage or Rogowski input mode must be enabled on flex models. Bit 0-1: Voltage Input Mode, 11b = 1/3 V. No other modes are supported. Bit 2: Rowgowski Input Mode Bit 3: unused Bit 4: System Calibrated (0=Flex) Read Only Bit Bit 5: unused Bit 6: unused Bit 7: unused Bits 8-15: unused |  |  | bitmap | Write: 3, 4 Read: 3, 4, 19, 20 | R/W | NV |  | 4182 | 1 | UInt
| · | · | PT Ratio - The meter scales this value by 100, so entering 200 yields a Potential Transformer ratio of 2:1. The default is 100 (1.00:1), which is no PT attached. Set this value before setting the System Voltage (below). |  |  |  | .01-320.00 | R/W | NV |  | 4183 | 1 | UInt |  | 100
| · | · | System Voltage – This voltage is Line to Line unless in System Type 10 (register 130), in which case it is Line to Neutral. This value is used to by the meter to calculate the full scale power for the analog outputs and pulse configuration (see below), and as full scale for phase loss (see register 142). The meter will refuse voltages that are outside the range of 82-660 volts when divided by the PT Ratio (above). |  |  |  | 82-32000 | R/W | NV |  | 4184 | 1 | UInt
| · | · | Theoretical Maximum System Power – This read only register is the theoretical maximum power the meter expects to see on a service. Its value is calculated by the meter from the System Type (register 130), CT size (register 131), and System Voltage (register 134). The register is updated whenever the user changes any of these parameters. This value is 100% of scale on the analog output (0-5VDC or 4-20mA), if equipped. It is also used to determine the maximum power the pulse outputs can keep up with. This integer register has the same scale as other integer power registers (see register 140 for power scaling). |  |  | kW | 1-32767 | R | NV |  | 4185 | 1 | UInt |  | W
| · | · | Neutral CT Primary: 1-12800 = CT Current Rating for the neutral current input. Not configurable on system calibrated models. |  |  | Amps | 1-12800 | R/W | NV |  | 4186 | 1 | UInt
| · | · | Reserved, Returns 0 |  |  |  |  | R |  |  | 4187 | 1 | UInt
| · | · | Scale Factor I (Current) | Scale Factors: These registers contain a signed integer, which scales the corresponding integer registers (see Scale column). Floating point registers are not scaled. Scaling is re-calculated whenever the meter configuration is changed. |  | integer | -10 to +10 | R |  |  | 4188 | 1 | SInt |  | -4 0.0001 -3 0.001 -2 0.01 -1 0.1 0 1.0 1 10.0 2 100.0 3 1000.0 4 10000.0
| · | · | Scale Factor V (Voltage) |  |  | integer |  | R |  |  | 4189 | 1 | SInt
| · | · | Scale Factor W (Power) |  |  | integer |  | R |  |  | 4190 | 1 | SInt
| · | · | Scale Factor E (Energy) |  |  | integer |  | R |  |  | 4191 | 1 | SInt
| · | · | Phase Loss Voltage Threshold: Set in percent of the System Voltage above. Default is 75 (75%). Set to 0 to disable the Phase Loss detection (both voltage and imbalance). |  | Phase Loss Output (if equipped) Note: The phases tested are determined by the System Type. | % | 0-99 | R/W | NV |  | 4192 | 1 | UInt
| · | · | Phase Loss Imbalance Threshold in Percent. Default is 25% phase to phase difference. For system type 40 (3 + N), both Line to Neutral and Line to Line voltages are tested. In System type 31, only Line to Line voltages are examined. In system type 12 (2 + N) just the two line to neutral voltages are compared. |  |  | % | 1-99 | R/W | NV |  | 4193 | 1 | UInt
| · | · | Wh (& VARh, if equipped) Energy per Pulse Output Contact Closure - Default is 1 KWh. If the meter cannot find a Pulse Duration that will keep up with the Maximum System Power (see register 135), It will reject the new value. If this is the case, check the meter configuration and/or try a larger value. |  | KWh & KVARh (if equipped) Pulse Contacts Note: The KWh pulse contact can keep up with a maximum power (Watts) of :1800000 x Wh pulse weight ÷ Contact Closure Duration (in mS) | Wh | 10000, 1000, 500, 250, 100, 10, 1 | R/W | NV |  | 4194 | 1 | UInt
| · | · | Pulse Contact Closure Duration in mS - This read only value is set by the meter to the slowest duration (in mS per closure) that will keep up with the Theoretical Maximum System Power (see register 135). Note that the open time is greater than or equal to the closure time, so the maximum pulse rate (Pulses Per Second) is the inverse of double the pulse time. |  |  | ms | 500, 250, 100, 50, 25, 10 | R | NV |  | 4195 | 1 | UInt
| · | · | Error Bitmap 1: 1 = Active: Bit 0: Phase A Voltage out of range Bit 1: Phase B Voltage out of range Bit 2: Phase C Voltage out of range Bit 3: Phase N Voltage out of range Bit 4: Phase A Current out of range Bit 5: Phase B Current out of range Bit 6: Phase C Current out of range Bit 7: Phase N Current out of range Bit 8: Phase Loss on Voltage Phase A Bit 9: Phase Loss on Voltage Phase B Bit 10: Phase Loss on Voltage Phase C Bit 11: Frequency out of the range of 45 – 65 Hz, or there is insufficient voltage on any phase to determine frequency. Bit 12: Low Power Factor on Phase A. Bit 13: Low Power Factor on Phase B. Bit 14: Low Power Factor on Phase C. Bit 15: Reserved, return 0. Note: Low Power Factor may indicate an extremely capacitive or inductive load, or that the Voltage and Current Phases are miss-connected, with one or more phases having a PF of less than 0.5. |  |  | Bitmap | 0-0xFFFF | R |  |  | 4196 | 1 | UInt
| · | · | Count of Energy Accumulator resets |  |  | count | 0-32767 | R | NV |  | 4197 | 1 | UInt
| · | · | Error Bitmap 2: 1 = Active: Bits 0 – 3: Reserved, return 0. Bit 4: Energy pulse output overrun error. Can only occur if the model has pulse outputs. The pulse output(s) are unable to keep up with the assigned accumulator (typically Total Real Energy). To fix, increase the Pulse Energy or reduce the Pulse Duration and reset the energy accumulators. Bit 5: Energy pulse output configuration error (present pulse energy setting may not keep up with the Theoretical Maximum System Power). To fix, Increase the Pulse Energy or reduce the Pulse Duration. Bit 6: unused, returns 0 Bit 7: unused, returns 0 Bits 8 - 11: Reserved, return 0. Bits 12 – 15: Reserved, return 0. |  |  | Bitmap | 0-0xFFFF | R |  |  | 4198 | 1 | UInt
|  | · | Number of Sub-Intervals per Demand Interval. Sets the number of sub-intervals that make a single demand interval. For block demand, set this to 1. Default is 1. When Sub-Interval Length register #150 is set to 0 (sync-to-comms mode), this register is ignored. |  | Demand Calculation | integer | 1-6 | R/W | NV |  | 4199 | 1 | UInt
|  | · | Sub-Interval Length in seconds. For external demand sync, set this register to 0 and then write 21211 to the command register to start each sub-interval. Default is 900 seconds (15 minutes). If logging is supported, this is also the Logging interval. |  |  | Seconds | 0, 10-32767 | R/W | NV |  | 4200 | 1 | UInt
| · | · | Meter Status Bitmap: Bit 0: True if demand interval synced to clock on minute or hour boundaries. If False Demand timer is free running. Bit 1: Meter Locked. This indicator is enabled if write access to the meter via Modbus has been locked via the user interface. Bit 2: Override LED on. This indicator is enabled if any of the rotary controls have been overriden via protocol communications. Bit 3: Reserved, returns 0. Bits 4 – 7: Reserved, return 0. Bits 8 - 11: Reserved, return 0. Bits 12 – 15: Reserved, return 0. |  |  | bitmap | 0-0xFFFF | R |  |  | 4201 | 1 | UInt
| · | · | Power Up Counter |  |  | count | 0-32767 | R | NV |  | 4202 | 1 | UInt
| · | · | Output Configuration Unless otherwise noted all units have an NO Energy contact and a NO or NC (Normally Open - Form A, or Closed-Form B) Phase Loss contact. | 3rd Output: 0 = RS-485 1 = RS-485 2 = VAR Pulse 3 = VAR Pulse 4 = 4-20mA 5 = 4-20mA 8 = 0-5VDC 9 = 0-5VDC 15 = Display Only | Phase Loss NC NO NC NO NC NO NC NO None | integer | 0-32767 | R | NV |  | 4203 | 1 | UInt
| · | · | Reserved, Returns 0 |  |  | integer | 0 | R |  |  | 4204 | 1 | UInt
|  | · | Date / Time Clock (RTC). If the meter's clock backup runs out, the RTC resets to: Day 01? Month 01? | Most Significant Byte (MSB) Day 1-31 (0x01-0x1F) | Least Significant Byte (LSB) Bits 0-3: Month 1-12 (0x01-0x0C) | Day / Month | See Bytes | R/W | NV |  | 4205 | 1 | UInt
|  | · | Hour 00? Year (20) 00? | Hour 0-23 (0x00-0x17) | Year 0-199 (0x00-0xC7) | Hour / Year | See Bytes | R/W | NV |  | 4206 | 1 | UInt
|  | · | Second 00? Minute 00? | Seconds 0-59 (0x00-0x3B) | Minutes 0-59 (0x00-0x3B) | Seconds / Minutes | See Bytes | R/W | NV |  | 4207 | 1 | UInt
|  | · | Device Address (Modbus RTU and BACnet MS/TP MAC Address) |  |  | integer | 1-247 | R | NV |  | 4208 | 1 | UInt
|  | · | Reserved, Returns 0 |  |  | Bitmap | 0 | R | NV |  | 4209 | 1 | UInt
|  | · | Baud Rate: Speeds above 38400 are not recommended for use with Modbus. They do not improve performance due to required Modbus protocol silent times, and may prevent the use of firmware update tools. The higher speeds are supported primarily for auto-bauding with BACnet protocol. When auto-bauding, the meter first determines the baud rate and parity. Only then can it determine the protocol. |  |  | integer | 4800, 9600, 19200, 38400, 57600, 76800, 115200 | R | NV |  | 4210 | 2 | ULong
|  | · | Reserved, Returns 0 |  |  | integer | 0 | R |  |  | 4212 | 16 | UInt
Meter Information |  |  | Null Terminated Text Strings, the first six are returned in the Modbus Report Slave ID and Read Device ID command responses. See Legend for format description | [7 empty] | 5000 | 496
| · | · | Manufacturer |  |  | ASCII | ASCII Text + Null | R | NV |  | 5000 | 32 | ASCII
| · | · | Model |  |  | ASCII | ASCII Text + Null | R | NV |  | 5032 | 32 | ASCII
| · | · | Name |  |  | ASCII | ASCII Text + Null | R | NV |  | 5064 | 32 | ASCII
| · | · | Data Set |  |  | ASCII | ASCII Text + Null | R | NV |  | 5096 | 32 | ASCII
| · | · | Serial Number |  |  | ASCII | ASCII Text + Null | R | NV |  | 5128 | 32 | ASCII
| · | · | Location: User assigned ASCII character string, typically to identify the meter's physical location. |  |  | ASCII | ASCII Text + Null | R/W | NV |  | 5160 | 32 | ASCII
| · | · | Expansion (optional) |  |  | ASCII | ASCII Text + Null | R | NV |  | 5192 | 32 | ASCII
| · | · | Date of Manufacture |  |  | ASCII | ASCII Text + Null | R | NV |  | 5224 | 32 | ASCII
| · | · | RS Version |  |  | ASCII | ASCII Text + Null | R | NV |  | 5256 | 32 | ASCII
| · | · | OS Version |  |  | ASCII | ASCII Text + Null | R | NV |  | 5288 | 32 | ASCII
| · | · | Product Revision |  |  | ASCII | ASCII Text + Null | R | NV |  | 5320 | 4 | ASCII
| · | · | Hardware Revision |  |  | ASCII | ASCII Text + Null | R | NV |  | 5324 | 4 | ASCII
Reset System (RS) |  |  | Firmware Downloader | [7 empty] | 7000 | 158
| · | · | Hardware Version |  |  |  | 0-32767 | R | NV |  | 7000 | 1 | UInt
| · | · | Firmware Version, Reset System (Boot Down Loader), 5 digits of the form 1.23.45 (Major.Minor.Revision) |  |  |  | 0-32767 | R | NV |  | 7001 | 1 | UInt
| · | · | Firmware Version, Operating System (Application), 5 digits of the form 1.23.45 (Major.Minor.Revision) |  |  |  | 0-32767 | R | NV |  | 7002 | 1 | UInt
| · | · | Device ID: 15035 |  |  |  | 0-32767 | R | NV |  | 7003 | 1 | UInt
| · | · | Modbus Address |  |  |  | 1-247 | R | NV |  | 7004 | 1 | UInt
| · | · | Baudrate |  |  |  | 1200, 2400, 4800, 9600, 19200, 38400 | R | NV |  | 7005 | 1 | UInt
| · | · | Password (always returns 0). Used only for download. |  |  |  |  | R | NV |  | 7006 | 1 | UInt
| · | · | Selftest (always returns 0) |  |  |  |  | R |  |  | 7007 | 1 | UInt
| · | · | PLOS (Power Logic Operating System). Returns the one’s complement of software’s safe vectors flag. Indicates if the Application (OS) or Boot (Downloader/Reset System) is running. |  |  |  | 0, 65535 | R |  |  | 7008 | 1 | UInt
| · | · | Command |  |  |  |  | R/W |  |  | 7009 | 1 | UInt
| · | · | Parameters |  |  |  |  | R/W |  |  | 7010 | 16 | UInt
| · | · | Status |  |  |  |  | R/W |  |  | 7026 | 1 | UInt
| · | · | Result |  |  |  |  | R/W |  |  | 7027 | 1 | UInt
| · | · | I/O Data |  |  |  |  | R/W |  |  | 7028 | 1 | UInt
| · | · | Data Area |  |  |  |  | R/W |  |  | 7029 | 128 | UInt
| · | · | Reserved, Returns 0x8000 (QNAN) |  |  |  | 0x8000 | R |  |  | 7157 | 1 | UInt
|  |  | Newest Logged Data to Oldest Data. 5760 entries (60 days with a 15 minute sub-interval). |  |  |  |  | R | NV |  | #REF! | 5760
|  |  | Reserved, Returns 0x8000 (QNAN) |  |  |  | 0x8000 | R |  |  | #REF! |  | UInt